## 1.audit
REPORT:Implementation of Electrical Savings Proposals: Addendum 1 |  |  |  | Compiled: | R. Wyma |  | Shared Energy Management(Pty)Ltd
|  |  |  | Date: | 2002-08-21 |  | PO Box 7270
Site Name: | Energy Audit DME-Building |  |  | Project No. | GP0032 |  | Centurion 0046
|  | Gross |  | Nett
Areas: | Total rented area | 13180 | m² | 10434.48 | m² | 79.17% | of gross
Occupancy: | Number of people in area | 440 | persons | 440 | persons
| Area per person | 29.9545 | m² / person | 23.7147 | m² / person
|  |  |  | indices |  | reference values: |  | Low | High
Energy: | Annual electricity consumption | 641025 | kWhr/year | 221.16 | MJ/m²/year |  |  | 500 | 1800
| Average monthly energy | 53418.75 | kWhr/mnth | 61.4333 | kWhr/m²/year |  |  | 140 | 500
| Average Maximum Demand | 426.4586 | kVA/mnth | 40.8701 | VA/m²/mnth |  |  | 45 | 120
| Maximum Maximum Demand | 523.2 | kVA/mnth | 50.1415 | VA/m²/mnth
| Load Factor |  |  | 0.13986 | Load Factor |  |  | 0.2 | 0.7
| Energy per person per year | 1456.875 | kWhr/person/year | 1456.875 | kWhr / person |  |  | 3000 | 6500
| Energy per person per 8 hr working day |  |  | 182.1094 | kWhr/pers/hr |  |  | 300 | 500
| Annual Energy consumption of Lights | 438528 | kWhr/year | 42.0268 | kWhr/m²/year
| Annual Energy consumption of Air Conditioning | -53823 | kWhr/year | -5.1582 | kWhr/m²/year
Costs: | Base year energy costs: |  |  | indices |  | reference values: |  | Low | High
| Consumption charge | 71025.57 | /year | 6.8068 | /m²
| Demand charge | 253469.955 | /year | 24.2916 | /m²
| Total electrical cost | 324495.525 | /year | 31.0984 | /m² |  |  | 40 | 100
| Total energy cost per unit of energy | 0.50621 | /kWhr
Metering: | Supply authority metering point | Tswane / Pretoria
| Present tariff | Maximum Demand
| Electricity consumption | 0.1108 | /kWhr
| Electricity demand | 49.53 | /kVA
Report: | Energy Savings Options | Max.Demand | Energy | DME | Capital | Pay- | Recommen-
|  | kVA Saving | kWhr Saving | Annual Saving | Cost (net) | back | dation
(years)
1.0 | Time-clock control on Lights | 0 | 153830.4 | 17044.4083 | 37500 | 2.2001 | yes
2.0 | Time-clock control on AC-units | 0 | 28315.2 | 3137.3242 | 62500 | 19.9214 | yes
3.0 | Demand control on AC-units | 49.268 | 0 | 29282.9244 | 100000 | 3.415 | yes
4.0 |  | 0 | 0
| Total for Recommended Options | 49.268 | 182145.6 | 49464.6569 | 200000 | 4.0433 | savings = | 4122.0547 | /month
|  |  |  | indices: |  | Low | High | % Less
Energy: | Revised yearly electricity consumption | 458879.4 | kWhr/year | 158.318 | MJ/m²/year | 500 | 1800 | 28.41%
| Revised average monthly energy | 38239.95 | kWhr/mnth | 43.9772 | kWhr/m²/year
| Revised average Maximum Demand | 377.1906 | kVA/mnth | 36.1485 | VA/m²/mnth | 45 | 120 | 11.55%
| Revised Maximum Maximum Demand | 473.932 | kVA/mnth | 45.4198 | VA/m²/mnth |  |  | 9.417%
| Revised Load Factor |  |  | 0.11053 | Load Factor | 0.2 | 0.8
| Revised Energy per person |  |  | 1042.9077 | kWhr / person | 3000 | 6500 | 28.41%
| Revised Energy per person per 8 hr working day |  |  | 130.3635 | kWhr/pers/hr | 300 | 500 | 28.41%
| Revised Annual Energy consumption of Lights | 284697.6 | kWhr/year | 27.2843 | kWhr/m²/year
| Revised Annual Energy consumption of AC | -82138.2 | kWhr/year | -7.8718 | kWhr/m²/year
Costs: | Revised consumption charge | 50843.8375 | /year | 4.8727 | /m² |  |  | 28.41%
| Revised demand charge | 224187.0306 | /year | 21.4852 | /m² |  |  | 11.55%
| Revised total electrical cost | 275030.8681 | /year | 26.3579 | /m² | 40 | 100 | 15.24%
| Revised total energy cost per unit of energy | 0.59935 | /kWhr
|  | 420 | kVA/mnth | 0.12472 | Load Factor

## 2.account
Tender: Energy Audit DME-building: Addendum 2
Department of Mineral and Energy Affairs
contractor: |  | Shared Energy Management (Pty)Ltd | [5 empty] | compiled: | R.Wyma
|  | PO Box 7270 | [5 empty] | date: | 2002-08-19
|  | Centurion 0046 | [5 empty] | ref: | GP0032
Subject: |  | Account Data for Electricity
Account Data for Maximum Demand (kVA)
| month | DME | DME % | 1999 | 2000 | 2001 | 2002 | average
| Jan | 576 | 36% | 1520 | 1440 | 1600 | 1600 | 1540
| Febr | 532.8 | 36% | 1520 | 1200 | 1480 | 1600 | 1450
| Mch | 508 | 34.79% | 1360 | 1400 | 1480 | 1600 | 1460
| Apr | 440 | 37.61% | 1120 | 1080 | 1200 | 1280 | 1170
| May | 442 | 40.55% | 1120 | 1200 | 920 | 1120 | 1090
| Jun | 0 | 0% | 1080 | 1160 | 1160 | 1160 | 1140
| Jul | 403 | 32.5% | 1080 | 1200 | 1440 |  | 1240
| Aug | 290.9036 | 29.09% | 1000 | 880 | 1000 |  | 960
| Sept | 436.8 | 36% | 1120 | 1400 | 1120 |  | 1213.3333
| Oct | 460.8 | 36% | 1120 | 1280 | 1240 |  | 1213.3333
| Nov | 504 | 36% | 1480 | 1200 | 1400 |  | 1360
| Dec | 523.2 | 36% | 1400 | 1600 | 1360 |  | 1453.3333
| Total | 5117.5036 | 36% | 14920 | 15040 | 15400 | 8360 | 15290
| Average | 426.4586 | 36% | 1243.3333 | 1253.3333 | 1283.3333 | 1393.3333 | 1274.1667
| Note: | 1. DME kVA for March to June calculated from client's invoice.
2. DME kVA for July based on measurements.
3. DME figures for the other months calculated on 36% average of building total.
Account Data for Energy Consumption (kWhr)
| month | DME | DME % | 1999 | 2000 | 2001 | 2002 | average
| Jan | 0 | 46% | 340000 | 288000 | 408000 | 340000 | 344000
| Febr | 0 | 46% | 384000 | 324000 | 292000 | 372000 | 343000
| Mch | 155854 | 54.12% | 264000 | 244000 | 276000 | 368000 | 288000
| Apr | 129725 | 45.04% | 240000 | 296000 | 292000 | 324000 | 288000
| May | 120524 | 45.65% | 260000 | 264000 | 240000 | 292000 | 264000
| Jun | 126788 | 43.55% | 276000 | 296000 | 280000 | 312558.1395 | 291139.5349
| Jul | 0 | 0% | 264000 | 284000 | 304000 |  | 284000
| Aug | 108134 | 37.67% | 244000 | 216000 | 320000 |  | 260000
| Sept | 0 | 37.67% | 272000 | 280000 | 248000 |  | 266666.6667
| Oct | 0 | 46% | 284000 | 288000 | 328000 |  | 300000
| Nov | 0 | 46% | 296000 | 240000 | 356000 |  | 297333.3333
| Dec | 0 | 46% | 268000 | 364000 | 340000 |  | 324000
| Total | 641025 | 46% | 3392000 | 3384000 | 3684000 | 2008558.1395 | 3550139.5349
| Average | 53418.75 | 46% | 282666.6667 | 282000 | 307000 | 334759.6899 | 295844.9612
| Note: | 1. DME kWhrs for March to June calculated from client's invoice.
2. DME kWhrs for July and Aug based on measurements.
3. DME figures for the other months calculated on 46% average of building total.

## 2.Mrt
DME Energy Audit: Addendum 2
contractor: |  | Shared Energy Management (Pty)Ltd | [11 empty] | compiled: | R.Wyma
|  | PO Box 7270 | [11 empty] | date: | 2002-08-08
|  | Centurion 0046 | [11 empty] | ref: | GP0032
Subject: |  | Electricity Consumption on each Distribution Board (DB)
Period: |  | 28 Feb to 30 Mrt 2002: Month March 2002
[5 empty] | Maximum Demand(MD) |  |  | Energy Consumption (kWhr) |  |  |  |  | Indices
| Floor | Block | Area | Reading | Factor | kVA | 2002-02-28 | 2002-03-30 | Factor | kWhr/mnth | MD / month |  | Energy / month
| Floor-3 | A | 500.56 | 480 | 80 | 38.4 | 9412 | 9516 | 80 | 8320 | 76.7141 | VA/m² | 16.6214 | kWhr / m²
|  | B | 248.88 |  |  |  | 967841 | 972121 | 1 | 4280 |  |  | 17.197 | kWhr / m²
|  | C | 693.28 | 460 | 120 | 55.2 | 6015 | 6102 | 120 | 10440 | 79.6215 | VA/m² | 15.0589 | kWhr / m²
|  | link | 216.3
| Floor-4 | A | 500.56 | 80 | 80 | 6.4 | 3530 | 3571 | 80 | 3280 | 12.7857 | VA/m² | 6.5527 | kWhr / m²
|  | B | 248.88 | 120 | 80 | 9.6 | 6402 | 6409 | 80 | 560 |  |  | 2.2501 | kWhr / m²
|  | C | 693.28 | 160 | 120 | 19.2 | 5536 | 5568 | 120 | 3840 | 27.6944 | VA/m² | 5.5389 | kWhr / m²
|  | link | 216.3
| Floor-5 | A | 500.56 | 360 | 80 | 28.8 | 3785 | 3863 | 80 | 6240 | 57.5356 | VA/m² | 12.466 | kWhr / m²
|  | B | 248.88 |  |  |  | 712573 | 718735 | 1 | 6162 |  |  | 24.7589 | kWhr / m²
|  | C | 693.28 | 260 | 120 | 31.2 | 1844 | 1903 | 120 | 7080 | 45.0035 | VA/m² | 10.2123 | kWhr / m²
|  | link | 216.3
| Floor-6 | A | 500.56 | 320 | 80 | 25.6 | 5035 | 5112 | 80 | 6160 | 51.1427 | VA/m² | 12.3062 | kWhr / m²
|  | B | 248.88 |  |  |  | 778205 | 781223 | 1 | 3018 |  |  | 12.1263 | kWhr / m²
|  | C | 693.28 | 220 | 120 | 26.4 | 8899 | 8952 | 120 | 6360 | 38.0799 | VA/m² | 9.1738 | kWhr / m²
|  | D | 376.96 | 200 | 60 | 12 | 5565 | 5586 | 60 | 1260 | 31.8336 | VA/m² | 3.3425 | kWhr / m²
|  | E | 360.16 | 150 | 60 | 9 | 9025 | 9071 | 60 | 2760 | 24.9889 | VA/m² | 7.6633 | kWhr / m²
|  | F | 370.96 | 200 | 60 | 12 | 7072 | 7157 | 60 | 5100 | 32.3485 | VA/m² | 13.7481 | kWhr / m²
|  | link | 304.7
| Floor-7 | A | 500.56 | 460 | 80 | 36.8 | 5825 | 6006 | 80 | 14480 | 73.5177 | VA/m² | 28.9276 | kWhr / m²
|  | B | 248.88 |  |  |  | 478458 | 481667 | 1 | 3209 |  |  | 12.8938 | kWhr / m²
|  | C | 693.28 | 340 | 120 | 40.8 | 8528 | 8612 | 120 | 10080 | 58.8507 | VA/m² | 14.5396 | kWhr / m²
|  | link | 216.3
| Floor-8 | A | 500.56 | 500 | 80 | 40 | 9405 | 9525 | 80 | 9600 | 79.9105 | VA/m² | 19.1785 | kWhr / m²
|  | B | 248.88 |  |  |  | 629595 | 632327 | 1 | 2732 |  |  | 10.9772 | kWhr / m²
|  | C | 693.28 | 420 | 120 | 50.4 | 8597 | 8718 | 120 | 14520 | 72.6979 | VA/m² | 20.9439 | kWhr / m²
|  | F | 370.96 | 300 | 60 | 18 | 6629 | 6695 | 60 | 3960 | 48.5228 | VA/m² | 10.675 | kWhr / m²
|  | link | 216.3
| Floor-9 | A | 500.56 | 300 | 80 | 24 | 11221 | 11301 | 80 | 6400 | 47.9463 | VA/m² | 12.7857 | kWhr / m²
|  | B | 248.88 |  |  |  | 648480 | 654773 | 1 | 6293 |  |  | 25.2853 | kWhr / m²
|  | C | 693.28 | 200 | 120 | 24 | 11943 | 12024 | 120 | 9720 | 34.618 | VA/m² | 14.0203 | kWhr / m²
|  | link | 216
|  | Total | 13180.28 |  |  | 507.8 |  |  |  | 155854 | 38.5273 | VA/m² | 11.8248 | kWhr / m²
Floors
|  | Total | #REF! |  |  | 1019 |  |  |  | 350972 | #REF! | VA/m² | #REF! | kWhr / m²
% of
|  | Total | #REF! |  |  | 49.83% |  |  |  | 44.41%

## 2.Apr
DME Energy Audit: Addendum 2
contractor: |  | Shared Energy Management (Pty)Ltd | [11 empty] | compiled: | R.Wyma
|  | PO Box 7270 | [11 empty] | date: | 2002-08-08
|  | Centurion 0046 | [11 empty] | ref: | GP0032
Subject: |  | Electricity Consumption on each Distribution Board (DB)
Period: |  | 30 Mrt to 30 Apr 2002: Month April 2002
[5 empty] | Maximum Demand(MD) |  |  | Energy Consumption (kWhr) |  |  |  |  | Indices
| Floor | Block | Area | Reading | Factor | kVA | 2002-03-30 | 2002-04-30 | Factor | kWhr/mnth | MD / month |  | Energy / month
| Floor-3 | A | 500.56 | 350 | 80 | 28 | 9516 | 9598 | 80 | 6560 | 55.9374 | VA/m² | 13.1053 | kWhr / m²
|  | B | 248.88 |  |  |  | 972121 | 975422 | 1 | 3301 |  |  | 13.2634 | kWhr / m²
|  | C | 693.28 | 400 | 120 | 48 | 6102 | 6182 | 120 | 9600 | 69.2361 | VA/m² | 13.8472 | kWhr / m²
|  | link | 216.3
| Floor-4 | A | 500.56 | 200 | 80 | 16 | 3571 | 3605 | 80 | 2720 | 31.9642 | VA/m² | 5.4339 | kWhr / m²
|  | B | 248.88 | 100 | 80 | 8 | 6409 | 6414 | 80 | 400 |  |  | 1.6072 | kWhr / m²
|  | C | 693.28 | 100 | 120 | 12 | 5568 | 5593 | 120 | 3000 | 17.309 | VA/m² | 4.3273 | kWhr / m²
|  | link | 216.3
| Floor-5 | A | 500.56 | 300 | 80 | 24 | 3863 | 3934 | 80 | 5680 | 47.9463 | VA/m² | 11.3473 | kWhr / m²
|  | B | 248.88 |  |  |  | 718735 | 723414 | 1 | 4679 |  |  | 18.8002 | kWhr / m²
|  | C | 693.28 | 200 | 120 | 24 | 1903 | 1949 | 120 | 5520 | 34.618 | VA/m² | 7.9622 | kWhr / m²
|  | link | 216.3
| Floor-6 | A | 500.56 | 300 | 80 | 24 | 5112 | 5172 | 80 | 4800 | 47.9463 | VA/m² | 9.5893 | kWhr / m²
|  | B | 248.88 |  |  |  | 781223 | 783929 | 1 | 2706 |  |  | 10.8727 | kWhr / m²
|  | C | 693.28 | 250 | 120 | 30 | 8952 | 9023 | 120 | 8520 | 43.2726 | VA/m² | 12.2894 | kWhr / m²
|  | D | 376.96 | 110 | 60 | 6.6 | 5586 | 5605 | 60 | 1140 | 17.5085 | VA/m² | 3.0242 | kWhr / m²
|  | E | 360.16 | 150 | 60 | 9 | 9071 | 9108 | 60 | 2220 | 24.9889 | VA/m² | 6.1639 | kWhr / m²
|  | F | 370.96 | 200 | 60 | 12 | 7157 | 7228 | 60 | 4260 | 32.3485 | VA/m² | 11.4837 | kWhr / m²
|  | link | 304.7
| Floor-7 | A | 500.56 | 200 | 80 | 16 | 6006 | 6172 | 80 | 13280 | 31.9642 | VA/m² | 26.5303 | kWhr / m²
|  | B | 248.88 |  |  |  | 481667 | 484063 | 1 | 2396 |  |  | 9.6271 | kWhr / m²
|  | C | 693.28 | 350 | 120 | 42 | 8612 | 8673 | 120 | 7320 | 60.5816 | VA/m² | 10.5585 | kWhr / m²
|  | link | 216.3
| Floor-8 | A | 500.56 | 350 | 80 | 28 | 9525 | 9596 | 80 | 5680 | 55.9374 | VA/m² | 11.3473 | kWhr / m²
|  | B | 248.88 |  |  |  | 632327 | 634819 | 1 | 2492 |  |  | 10.0129 | kWhr / m²
|  | C | 693.28 | 400 | 120 | 48 | 8718 | 8814 | 120 | 11520 | 69.2361 | VA/m² | 16.6167 | kWhr / m²
|  | F | 370.96 | 200 | 60 | 12 | 6695 | 6743 | 60 | 2880 | 32.3485 | VA/m² | 7.7636 | kWhr / m²
|  | link | 216.3
| Floor-9 | A | 500.56 | 200 | 80 | 16 | 11301 | 11365 | 80 | 5120 | 31.9642 | VA/m² | 10.2285 | kWhr / m²
|  | B | 248.88 |  |  |  | 654773 | 659344 | 1 | 4571 |  |  | 18.3663 | kWhr / m²
|  | C | 693.28 | 300 | 120 | 36 | 12024 | 12102 | 120 | 9360 | 51.9271 | VA/m² | 13.501 | kWhr / m²
|  | link | 216
|  | Total | 13180.28 |  |  | 439.6 |  |  |  | 129725 | 33.3529 | VA/m² | 9.8424 | kWhr / m²
Floors
|  | Total | #REF! |  |  | 858 |  |  |  | 298516 | #REF! | VA/m² | #REF! | kWhr / m²
% of
|  | Total | #REF! |  |  | 51.24% |  |  |  | 43.46%

## 2.May
DME Energy Audit: Addendum 2
contractor: |  | Shared Energy Management (Pty)Ltd | [11 empty] | compiled: | R.Wyma
|  | PO Box 7270 | [11 empty] | date: | 2002-08-08
|  | Centurion 0046 | [11 empty] | ref: | GP0032
Subject: |  | Electricity Consumption on each Distribution Board (DB)
Period: |  | 30 Apr to 30 May 2002: Month May 2002
[5 empty] | Maximum Demand(MD) |  |  | Energy Consumption (kWhr) |  |  |  |  | Indices
| Floor | Block | Area | Reading | Factor | kVA | 2002-04-30 | 2002-05-30 | Factor | kWhr/mnth | MD / month |  | Energy / month
| Floor-3 | A | 500.56 | 360 | 80 | 28.8 | 9598 | 9687 | 80 | 7120 | 57.5356 | VA/m² | 14.2241 | kWhr / m²
|  | B | 248.88 |  |  |  | 975422 | 979081 | 1 | 3659 |  |  | 14.7019 | kWhr / m²
|  | C | 693.28 | 360 | 120 | 43.2 | 6182 | 6247 | 120 | 7800 | 62.3125 | VA/m² | 11.2509 | kWhr / m²
|  | link | 216.3
| Floor-4 | A | 500.56 | 260 | 80 | 20.8 | 3605 | 3642 | 80 | 2960 | 41.5535 | VA/m² | 5.9134 | kWhr / m²
|  | B | 248.88 | 100 | 80 | 8 | 6414 | 6419 | 80 | 400 |  |  | 1.6072 | kWhr / m²
|  | C | 693.28 | 100 | 120 | 12 | 5593 | 5618 | 120 | 3000 | 17.309 | VA/m² | 4.3273 | kWhr / m²
|  | link | 216.3
| Floor-5 | A | 500.56 | 280 | 80 | 22.4 | 3934 | 3993 | 80 | 4720 | 44.7499 | VA/m² | 9.4294 | kWhr / m²
|  | B | 248.88 |  |  |  | 723414 | 728029 | 1 | 4615 |  |  | 18.5431 | kWhr / m²
|  | C | 693.28 | 200 | 120 | 24 | 1949 | 1998 | 120 | 5880 | 34.618 | VA/m² | 8.4814 | kWhr / m²
|  | link | 216.3
| Floor-6 | A | 500.56 | 280 | 80 | 22.4 | 5172 | 5231 | 80 | 4720 | 44.7499 | VA/m² | 9.4294 | kWhr / m²
|  | B | 248.88 |  |  |  | 783929 | 786937 | 1 | 3008 |  |  | 12.0861 | kWhr / m²
|  | C | 693.28 | 260 | 120 | 31.2 | 9023 | 9073 | 120 | 6000 | 45.0035 | VA/m² | 8.6545 | kWhr / m²
|  | D | 376.96 | 180 | 60 | 10.8 | 5605 | 5634 | 60 | 1740 | 28.6503 | VA/m² | 4.6159 | kWhr / m²
|  | E | 360.16 | 180 | 60 | 10.8 | 9108 | 9144 | 60 | 2160 | 29.9867 | VA/m² | 5.9973 | kWhr / m²
|  | F | 370.96 | 200 | 60 | 12 | 7228 | 7304 | 60 | 4560 | 32.3485 | VA/m² | 12.2924 | kWhr / m²
|  | link | 304.7
| Floor-7 | A | 500.56 | 360 | 80 | 28.8 | 6172 | 6307 | 80 | 10800 | 57.5356 | VA/m² | 21.5758 | kWhr / m²
|  | B | 248.88 |  |  |  | 484063 | 487035 | 1 | 2972 |  |  | 11.9415 | kWhr / m²
|  | C | 693.28 | 360 | 120 | 43.2 | 8673 | 8730 | 120 | 6840 | 62.3125 | VA/m² | 9.8661 | kWhr / m²
|  | link | 216.3
| Floor-8 | A | 500.56 | 280 | 80 | 22.4 | 9596 | 9655 | 80 | 4720 | 44.7499 | VA/m² | 9.4294 | kWhr / m²
|  | B | 248.88 |  |  |  | 634819 | 636878 | 1 | 2059 |  |  | 8.2731 | kWhr / m²
|  | C | 693.28 | 340 | 120 | 40.8 | 8814 | 8907 | 120 | 11160 | 58.8507 | VA/m² | 16.0974 | kWhr / m²
|  | F | 370.96 | 200 | 60 | 12 | 6743 | 6796 | 60 | 3180 | 32.3485 | VA/m² | 8.5724 | kWhr / m²
|  | link | 216.3
| Floor-9 | A | 500.56 | 240 | 80 | 19.2 | 11365 | 11424 | 80 | 4720 | 38.357 | VA/m² | 9.4294 | kWhr / m²
|  | B | 248.88 |  |  |  | 659344 | 662795 | 1 | 3451 |  |  | 13.8661 | kWhr / m²
|  | C | 693.28 | 240 | 120 | 28.8 | 12102 | 12171 | 120 | 8280 | 41.5417 | VA/m² | 11.9432 | kWhr / m²
|  | link | 216
|  | Total | 13180.28 |  |  | 441.6 |  |  |  | 120524 | 33.5046 | VA/m² | 9.1443 | kWhr / m²
Floors
|  | Total | #REF! |  |  | 821 |  |  |  | 285785 | #REF! | VA/m² | #REF! | kWhr / m²
% of
|  | Total | #REF! |  |  | 53.79% |  |  |  | 42.17%

## 2.June
DME Energy Audit: Addendum 2
contractor: |  | Shared Energy Management (Pty)Ltd | [11 empty] | compiled: | R.Wyma
|  | PO Box 7270 | [11 empty] | date: | 2002-08-08
|  | Centurion 0046 | [11 empty] | ref: | GP0032
Subject: |  | Electricity Consumption on each Distribution Board (DB)
Period: |  | 30 May to 30 June 2002: Month June 2002
[5 empty] | Maximum Demand(MD) |  |  | Energy Consumption (kWhr) |  |  |  |  | Indices
| Floor | Block | Area | Reading | Factor | kVA | 2002-05-30 | 2002-06-30 | Factor | kWhr/mnth | MD / month |  | Energy / month
| Floor-3 | A | 500.56 | 400 | 80 | 32 | 9687 | 9788 | 80 | 8080 | 63.9284 | VA/m² | 16.1419 | kWhr / m²
|  | B | 248.88 |  |  |  | 979081 | 983245 | 1 | 4164 |  |  | 16.731 | kWhr / m²
|  | C | 693.28 | 350 | 120 | 42 | 6247 | 6321 | 120 | 8880 | 60.5816 | VA/m² | 12.8087 | kWhr / m²
|  | link | 216.3
| Floor-4 | A | 500.56 | 100 | 80 | 8 | 3642 | 3679 | 80 | 2960 | 15.9821 | VA/m² | 5.9134 | kWhr / m²
|  | B | 248.88 | 100 | 80 | 8 | 6419 | 6422 | 80 | 240 |  |  | 0.96432 | kWhr / m²
|  | C | 693.28 | 100 | 120 | 12 | 5618 | 5648 | 120 | 3600 | 17.309 | VA/m² | 5.1927 | kWhr / m²
|  | link | 216.3
| Floor-5 | A | 500.56 | 350 | 80 | 28 | 3993 | 4065 | 80 | 5760 | 55.9374 | VA/m² | 11.5071 | kWhr / m²
|  | B | 248.88 |  |  |  | 728029 | 734233 | 1 | 6204 |  |  | 24.9277 | kWhr / m²
|  | C | 693.28 | 200 | 120 | 24 | 1998 | 2055 | 120 | 6840 | 34.618 | VA/m² | 9.8661 | kWhr / m²
|  | link | 216.3
| Floor-6 | A | 500.56 | 300 | 80 | 24 | 5231 | 5297 | 80 | 5280 | 47.9463 | VA/m² | 10.5482 | kWhr / m²
|  | B | 248.88 |  |  |  | 786937 | 790846 | 1 | 3909 |  |  | 15.7064 | kWhr / m²
|  | C | 693.28 | 300 | 120 | 36 | 9073 | 9133 | 120 | 7200 | 51.9271 | VA/m² | 10.3854 | kWhr / m²
|  | D | 376.96 | 200 | 60 | 12 | 5634 | 5671 | 60 | 2220 | 31.8336 | VA/m² | 5.8892 | kWhr / m²
|  | E | 360.16 | 250 | 60 | 15 | 9144 | 9211 | 60 | 4020 | 41.6482 | VA/m² | 11.1617 | kWhr / m²
|  | F | 370.96 | 200 | 60 | 12 | 7304 | 7359 | 60 | 3300 | 32.3485 | VA/m² | 8.8958 | kWhr / m²
|  | link | 304.7
| Floor-7 | A | 500.56 | 300 | 80 | 24 | 6307 | 6446 | 80 | 11120 | 47.9463 | VA/m² | 22.2151 | kWhr / m²
|  | B | 248.88 |  |  |  | 487035 | 489038 | 1 | 2003 |  |  | 8.0481 | kWhr / m²
|  | C | 693.28 | 200 | 120 | 24 | 8730 | 8784 | 120 | 6480 | 34.618 | VA/m² | 9.3469 | kWhr / m²
|  | link | 216.3
| Floor-8 | A | 500.56 | 350 | 80 | 28 | 9655 | 9714 | 80 | 4720 | 55.9374 | VA/m² | 9.4294 | kWhr / m²
|  | B | 248.88 |  |  |  | 636878 | 639350 | 1 | 2472 |  |  | 9.9325 | kWhr / m²
|  | C | 693.28 | 250 | 120 | 30 | 8907 | 8976 | 120 | 8280 | 43.2726 | VA/m² | 11.9432 | kWhr / m²
|  | F | 370.96 | 200 | 60 | 12 | 6796 | 6841 | 60 | 2700 | 32.3485 | VA/m² | 7.2784 | kWhr / m²
|  | link | 216.3
| Floor-9 | A | 500.56 | 100 | 80 | 8 | 11424 | 11490 | 80 | 5280 | 15.9821 | VA/m² | 10.5482 | kWhr / m²
|  | B | 248.88 |  |  |  | 662795 | 666791 | 1 | 3996 |  |  | 16.0559 | kWhr / m²
|  | C | 693.28 | 200 | 120 | 24 | 12171 | 12230 | 120 | 7080 | 34.618 | VA/m² | 10.2123 | kWhr / m²
|  | link | 216
|  | Total | 13180.28 |  |  | 403 |  |  |  | 126788 | 30.576 | VA/m² | 9.6195 | kWhr / m²
Floors
|  | Total | #REF! |  |  | 772 |  |  |  | 309714 | #REF! | VA/m² | #REF! | kWhr / m²
% of
|  | Total | #REF! |  |  | 52.2% |  |  |  | 40.94%

## 2.July-SEM
DME Energy Audit: Addendum 2
contractor: |  | Shared Energy Management (Pty)Ltd | [11 empty] | compiled: | R.Wyma
|  | PO Box 7270 | [11 empty] | date: | 2002-08-08
|  | Centurion 0046 | [11 empty] | ref: | GP0032
Subject: |  | Electricity Consumption on each Distribution Board (DB)
Period: |  | 23 July to 16 Aug. 2002: Prorata adjusted to 30 days
[5 empty] | Maximum Demand(MD) |  |  | Energy Consumption (kWhr) |  |  |  |  | Indices
| Floor | Block | Area | Reading | Factor | kVA | 2002-07-23 | 2002-08-16 | Factor | kWhr/mnth | MD / month |  | Energy / month
| Floor-3 | A | 500.56 | 400 | 80 | 32 | 9883 | 9946 | 80 | 6510 | 63.9284 | VA/m² | 13.0054 | kWhr / m²
|  | B | 248.88 |  |  |  | 987502 | 990663 | 1 | 4082.9583 |  |  | 16.4053 | kWhr / m²
|  | C | 693.28 | 310 | 120 | 37.2 | 6386 | 6434 | 120 | 7440 | 53.658 | VA/m² | 10.7316 | kWhr / m²
|  | link | 216.3
| Floor-4 | A | 500.56 | 180 | 80 | 14.4 | 3726 | 3756 | 80 | 3100 | 28.7678 | VA/m² | 6.1931 | kWhr / m²
|  | B | 248.88 | 100 | 80 | 8 | 6424 | 6426 | 80 | 206.6667 |  |  | 0.83039 | kWhr / m²
|  | C | 693.28 | 80 | 120 | 9.6 | 5675 | 5692 | 120 | 2635 | 13.8472 | VA/m² | 3.8008 | kWhr / m²
|  | link | 216.3
| Floor-5 | A | 500.56 | 220 | 80 | 17.6 | 4128 | 4166 | 80 | 3926.6667 | 35.1606 | VA/m² | 7.8445 | kWhr / m²
|  | B | 248.88 |  |  |  | 739525 | 743285 | 1 | 4856.6667 |  |  | 19.5141 | kWhr / m²
|  | C | 693.28 | 180 | 120 | 21.6 | 2102 | 2140 | 120 | 5890 | 31.1562 | VA/m² | 8.4958 | kWhr / m²
|  | link | 216.3
| Floor-6 | A | 500.56 | 280 | 80 | 22.4 | 5350 | 5389 | 80 | 4030 | 44.7499 | VA/m² | 8.051 | kWhr / m²
|  | B | 248.88 |  |  |  | 794287 | 796495 | 1 | 2852 |  |  | 11.4593 | kWhr / m²
|  | C | 693.28 | 200 | 120 | 24 | 9184 | 9221 | 120 | 5735 | 34.618 | VA/m² | 8.2723 | kWhr / m²
|  | D | 376.96 | 180 | 60 | 10.8 | 5707 | 5728 | 60 | 1627.5 | 28.6503 | VA/m² | 4.3174 | kWhr / m²
|  | E | 360.16 | 160 | 60 | 9.6 | 9264 | 9302 | 60 | 2945 | 26.6548 | VA/m² | 8.1769 | kWhr / m²
|  | F | 370.96 | 140 | 60 | 8.4 | 7405 | 7435 | 60 | 2325 | 22.644 | VA/m² | 6.2675 | kWhr / m²
|  | link | 304.7
| Floor-7 | A | 500.56 | 260 | 80 | 20.8 | 6548 | 6643 | 80 | 9816.6667 | 41.5535 | VA/m² | 19.6114 | kWhr / m²
|  | B | 248.88 |  |  |  | 490684 | 492493 | 1 | 2336.625 |  |  | 9.3886 | kWhr / m²
|  | C | 693.28 | 220 | 120 | 26.4 | 8826 | 8864 | 120 | 5890 | 38.0799 | VA/m² | 8.4958 | kWhr / m²
|  | link | 216.3
| Floor-8 | A | 500.56 | 300 | 80 | 24 | 9777 | 9824 | 80 | 4856.6667 | 47.9463 | VA/m² | 9.7025 | kWhr / m²
|  | B | 248.88 |  |  |  | 640994 | 642862 | 1 | 2412.8333 |  |  | 9.6948 | kWhr / m²
|  | C | 693.28 | 200 | 120 | 24 | 9032 | 9078 | 120 | 7130 | 34.618 | VA/m² | 10.2844 | kWhr / m²
|  | F | 370.96 | 120 | 60 | 7.2 | 6872 | 6901 | 60 | 2247.5 | 19.4091 | VA/m² | 6.0586 | kWhr / m²
|  | link | 216.3
| Floor-9 | A | 500.56 | 160 | 80 | 12.8 | 1544 | 1592 | 80 | 4960 | 25.5714 | VA/m² | 9.9089 | kWhr / m²
|  | B | 248.88 |  |  |  | 670457 | 673168 | 1 | 3501.7083 |  |  | 14.0699 | kWhr / m²
|  | C | 693.28 | 180 | 120 | 21.6 | 2278 | 2322 | 120 | 6820 | 31.1562 | VA/m² | 9.8373 | kWhr / m²
|  | link | 216
|  | Total | 13180.28 |  |  | 352.4 |  |  |  | 108134.4583 | 26.7369 | VA/m² | 8.2043 | kWhr / m²
Floors
|  | Total | #REF! |  |  | 772 |  |  |  | 309714 | #REF! | VA/m² | #REF! | kWhr / m²
% of
|  | Total | #REF! |  |  | 45.65% |  |  |  | 34.91%

## 3.Year
Tender: Energy Audit DME-building: Addendum 3
Department of Mineral and Energy Affairs
contractor: |  | Shared Energy Management (Pty)Ltd |  |  |  |  | compiled: | R.Wyma
|  | PO Box 7270 |  |  |  |  | date: | 2002-08-19
|  | Centurion 0046 |  |  |  |  | ref: | GP0032
Subject: |  | Estimate of Year Profile for Lights, Plugs and AC
Data for Maximum Demand (kVA)
| month | DME | Lights | Plugs | AC | % AC of DME
| Jan | 576 | 173 | 102 | 301 | 52.26%
| Febr | 532.8 | 173 | 102 | 257.8 | 48.39%
| Mch | 508 | 173 | 102 | 233 | 45.87%
| Apr | 440 | 173 | 102 | 165 | 37.5%
| May | 442 | 173 | 102 | 167 | 37.78%
| Jun | 0 | 173 | 102 | -275 | #DIV/0!
| Jul | 403 | 173 | 102 | 128 | 31.76%
| Aug | 290.9036 | 173 | 102 | 15.9036 | 5.467%
| Sept | 436.8 | 173 | 102 | 161.8 | 37.04%
| Oct | 460.8 | 173 | 102 | 185.8 | 40.32%
| Nov | 504 | 173 | 102 | 229 | 45.44%
| Dec | 523.2 | 173 | 102 | 248.2 | 47.44%
| Total | 5117.5036 | 2076 | 1224 | 1817.5036 | 35.52%
| Average | 426.4586 | 173 | 102 | 151.4586 | 35.52%
| Note: | 1. The measured MD for AC in July , Aug = 207 kW.
2. "AC" is calculated, assuming "Lights" and "Plugs" will be constant through the year.
3. See "Account Data" for calculation of "DME"-figures.
| Result: | 1. The DME maximum demand as per the bill from the owner is LOW.
Data for Energy Consumption (kWhr)
| month | DME | Lights | Plugs | AC | % AC of DME
| Jan | 0 | 36544 | 21360 | -57904 | #DIV/0!
| Febr | 0 | 36544 | 21360 | -57904 | #DIV/0!
| Mch | 155854 | 36544 | 21360 | 97950 | 62.85%
| Apr | 129725 | 36544 | 21360 | 71821 | 55.36%
| May | 120524 | 36544 | 21360 | 62620 | 51.96%
| Jun | 126788 | 36544 | 21360 | 68884 | 54.33%
| Jul | 0 | 36544 | 21360 | -57904 | #DIV/0!
| Aug | 108134 | 36544 | 21360 | 50230 | 46.45%
| Sept | 0 | 36544 | 21360 | -57904 | #DIV/0!
| Oct | 0 | 36544 | 21360 | -57904 | #DIV/0!
| Nov | 0 | 36544 | 21360 | -57904 | #DIV/0!
| Dec | 0 | 36544 | 21360 | -57904 | #DIV/0!
| Total | 641025 | 438528 | 256320 | -53823 | #DIV/0!
| Average | 53418.75 | 36544 | 21360 | -4485.25 | -8.396%
| Note: | 1. The energy balance for July, Aug is in order, compared to the measured
quantity of 50 704 kWhrs
2. "AC" is calculated, assuming "Lights" and "Plugs" will be constant through the year.
3. DME kWhrs for March to June calculated from client's invoice.
4. DME kWhrs for July and Aug based on measurements.
5. See "Account Data" for calculation of "DME"-figures.
6. Energy consumption of Lights and Plugs from "Inventory List": Addendum 4.
| Result: | 1. Energy balance of the building is acceptable.
2. An average of 57% of the energy consumption is used for AC.

## 4.invent
DME Energy Audit: Addendum 4
contractor: |  | Shared Energy Management (Pty)Ltd | [12 empty] | compiled: | R.Wyma
|  | PO Box 7270 | [12 empty] | date: | 2002-08-08
|  | Centurion 0046 | [12 empty] | ref: | GP0032
Subject: |  | Inventory List of Equipment
|  |  | Areas (m²) |  |  | Quantity |  |  | Power Rating (kW) |  |  |  | Measured Power (kW)
| Floor | Block | Gross | Net | Lights | Plugs | AC | Lights | Plugs | AC | Total | Lights | Plugs | AC | Total
| Floor-3 | A | 500.56 | 452.56 | 40 | 36 | 36 | 7.68 | 9 | 72 | 88.68 | 4 | 4 | 7.5 | 15.5
|  | B | 248.88 | 227.28 | 21 | 10 | 10 | 4.02 | 2.5 | 20 | 26.52 | 10.5 | 3 | 6 | 19.5
|  | C | 693.28 | 620.08 | 57 | 27 | 25 | 10.92 | 6.75 | 50 | 67.67 | 14.5 | 3 | 11 | 28.5
|  | link | 216.3
| Floor-4 | A | 500.56 | 452.56 | 40 | 33 | 32 | 7.68 | 8.25 | 64 | 79.93 | 5 | 4 | 6 | 15
|  | B | 248.88 | 227.28 | 21 | 14 | 12 | 4.02 | 3.5 | 24 | 31.52 | 6 | 3.5 | 3.5 | 13
|  | C | 693.28 | 620.08 | 57 | 8 | 22 | 10.92 | 2 | 44 | 56.92 | 8 | 3.5 | 7 | 18.5
|  | link | 216.3
| Floor-5 | A | 500.56 | 452.56 | 40 | 30 | 34 | 7.68 | 7.5 | 68 | 83.18 | 6 | 3 | 11 | 20
|  | B | 248.88 | 227.28 | 33 | 15 | 15 | 4.02 | 3.75 | 30 | 37.77 | 5.5 | 4 | 6 | 15.5
|  | C | 693.28 | 620.08 | 57 | 20 | 24 | 10.92 | 5 | 48 | 63.92 | 9 | 3 | 9 | 21
|  | link | 216.3
| Floor-6 | A | 500.56 | 452.56 | 54 | 10 | 34 | 10.2 | 2.5 | 68 | 80.7 | 4.5 | 8 | 1 | 13.5
|  | B | 248.88 | 227.28 | 21 | 13 | 13 | 6.18 | 3.25 | 26 | 35.43 | 6.5 | 6.5 | 5 | 18
|  | C | 693.28 | 620.08 | 104 | 20 | 24 | 19.38 | 5 | 48 | 72.38 | 14 | 3 | 3 | 20
|  | D | 376.96 | 340.96 | 33 | 10 | 11 | 6.42 | 2.5 | 22 | 30.92 | 4 | 2 | 2 | 8
|  | E | 360.16 | 324.16 | 32 | 9 | 7 | 6.24 | 2.25 | 14 | 22.49 | 4.5 | 1 | 3 | 8.5
|  | F | 370.96 | 334.96 | 32 | 10 | 14 | 6.24 | 2.5 | 28 | 36.74 | 4 | 3 | 3 | 10
|  | link | 304.7
| Floor-7 | A | 500.56 | 452.56 | 40 | 35 | 31 | 7.68 | 8.75 | 62 | 78.43 | 7 | 5.5 | 10 | 22.5
|  | B | 248.88 | 227.28 | 21 | 4 | 5 | 4.02 | 1 | 10 | 15.02 | 5.5 | 4 | 10 | 19.5
|  | C | 693.28 | 620.08 | 57 | 27 | 23 | 10.92 | 6.75 | 46 | 63.67 | 8 | 4 | 14 | 26
|  | link | 216.3
| Floor-8 | A | 500.56 | 452.56 | 40 | 29 | 32 | 7.68 | 7.25 | 64 | 78.93 | 6 | 4 | 8 | 18
|  | B | 248.88 | 227.28 | 21 | 0 | 7 | 4.02 | 0 | 14 | 18.02 | 6 | 3 | 6 | 15
|  | C | 693.28 | 620.08 | 57 | 19 | 23 | 10.92 | 4.75 | 46 | 61.67 | 7 | 3 | 15 | 25
|  | F | 370.96 | 334.96 | 32 | 17 | 15 | 6.24 | 4.25 | 30 | 40.49 | 4 | 4 | 3 | 11
|  | link | 216.3
| Floor-9 | A | 500.56 | 452.56 | 40 | 17 | 26 | 7.68 | 4.25 | 52 | 63.93 | 5.5 | 3 | 7 | 15.5
|  | B | 248.88 | 227.28 | 21 | 0 | 8 | 4.02 | 0 | 16 | 20.02 | 6 | 7 | 4 | 17
|  | C | 693.28 | 620.08 | 57 | 13 | 20 | 10.92 | 3.25 | 40 | 54.17 | 10 | 3 | 10 | 0
|  | link | 216 |  |  |  |  | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW)
|  | Total | 13180.28 | 10434.48 | 1028 | 426 | 434 | 196.62 | 106.5 | 1006 | 1309.12 | 171 | 95 | 171 | 414
[8 empty] | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW)
[7 empty] | Load per m² (W/m²) | 18.8433 | 10.2065 | 96.4111 | 125.461 | 16.388 | 9.1044 | 16.388 | 39.6762
(10 434 m²)
[11 empty] | % of Total Rated Power | 86.97% | 89.2% | 17% | 31.62%
From "Total" above:
[11 empty] | Estimated day-time kWhrs | 27360 | 15200 | 27360 | 69920
(80% 10hrs/day, 20 days)
From Addendum 5:
[11 empty] | Estimated night-time kWhrs | 9184 | 6160 | 15008 | 30352
(80% 14hrs/day, 20 days)
[11 empty] | Estimated Total kWhrs (July) | 36544 | 21360 | 42368 | 100272
| Notes: | 1. The total estimated kWhrs of |  |  |  | 100272 | kWhrs | compares well with the acount data in Addendum 2.
2. Of the 434 AC-units, 109 units are AC-mid wall split units.
3. Building occupation is 440 people.
0

## 5.night savings
DME Energy Audit: Addendum 5
contractor: |  | Shared Energy Management (Pty)Ltd | [13 empty] | compiled: | R.Wyma
|  | PO Box 7270 | [13 empty] | date: | 2002-08-08
|  | Centurion 0046 | [13 empty] | ref: | GP0032
Subject: |  | Energy Saving Potential on Switching of Lights, Plugs and AC at Night-Time
|  |  | Areas (m²) |  | Measured Power (kW): Night-Time |  |  |  | Potential Minimum Power (kW) |  |  |  | Potential Saving (kW)
| Floor | Block | Gross | Net | Lights | Plugs | AC | Total | Lights | Plugs | AC | Total | Lights | Plugs | AC | Total
| Floor-3 | A | 500.56 | 452.56 | 1 | 0.5 | 3 | 4.5 | 1 | 0.5 | 0 | 1.5 | 0 | 0 | 3 | 3
|  | B | 248.88 | 227.28 | 0.5 | 0.5 | 3.5 | 4.5 | 0.5 | 0.5 | 0 | 1 | 0 | 0 | 3.5 | 3.5
|  | C | 693.28 | 620.08 | 1.5 | 1.5 | 3 | 6 | 1 | 1.5 | 0 | 2.5 | 0.5 | 0 | 3 | 3.5
|  | link | 216.3
| Floor-4 | A | 500.56 | 452.56 | 1.5 | 0.5 | 3.5 | 5.5 | 1 | 0.5 | 0 | 1.5 | 0.5 | 0 | 3.5 | 4
|  | B | 248.88 | 227.28 | 4 | 3 | 3.5 | 10.5 | 1 | 3 | 0 | 4 | 3 | 0 | 3.5 | 6.5
|  | C | 693.28 | 620.08 | 0.5 | 0.5 | 3.5 | 4.5 | 0.5 | 0.5 | 0 | 1 | 0 | 0 | 3.5 | 3.5
|  | link | 216.3
| Floor-5 | A | 500.56 | 452.56 | 0.5 | 2.5 | 0.5 | 3.5 | 0.5 | 2.5 | 0 | 3 | 0 | 0 | 0.5 | 0.5
|  | B | 248.88 | 227.28 | 1.5 | 0.5 | 4 | 6 | 1 | 0.5 | 0 | 1.5 | 0.5 | 0 | 4 | 4.5
|  | C | 693.28 | 620.08 | 1.5 | 1 | 2.5 | 5 | 1 | 1 | 0 | 2 | 0.5 | 0 | 2.5 | 3
|  | link | 216.3
| Floor-6 | A | 500.56 | 452.56 | 0.5 | 0.5 | 1.5 | 2.5 | 0.5 | 0.5 | 0 | 1 | 0 | 0 | 1.5 | 1.5
|  | B | 248.88 | 227.28 | 1 | 0.5 | 0.5 | 2 | 1 | 0.5 | 0 | 1.5 | 0 | 0 | 0.5 | 0.5
|  | C | 693.28 | 620.08 | 1.5 | 0.5 | 3.5 | 5.5 | 1 | 0.5 | 0 | 1.5 | 0.5 | 0 | 3.5 | 4
|  | D | 376.96 | 340.96 | 2 | 1 | 1 | 4 | 1 | 1 | 0 | 2 | 1 | 0 | 1 | 2
|  | E | 360.16 | 324.16 | 1 | 0.5 | 1 | 2.5 | 1 | 0.5 | 0 | 1.5 | 0 | 0 | 1 | 1
|  | F | 370.96 | 334.96 | 1 | 1 | 1 | 3 | 1 | 1 | 0 | 2 | 0 | 0 | 1 | 1
|  | link | 304.7
| Floor-7 | A | 500.56 | 452.56 | 5.5 | 2 | 8 | 15.5 | 1 | 2 | 0 | 3 | 4.5 | 0 | 8 | 12.5
|  | B | 248.88 | 227.28 | 1 | 0.5 | 0.5 | 2 | 1 | 0.5 | 0 | 1.5 | 0 | 0 | 0.5 | 0.5
|  | C | 693.28 | 620.08 | 0.5 | 2 | 4.5 | 7 | 0.5 | 2 | 0 | 2.5 | 0 | 0 | 4.5 | 4.5
|  | link | 216.3
| Floor-8 | A | 500.56 | 452.56 | 0.5 | 1.5 | 3 | 5 | 0.5 | 1.5 | 0 | 2 | 0 | 0 | 3 | 3
|  | B | 248.88 | 227.28 | 1 | 1 | 3.5 | 5.5 | 1 | 1 | 0 | 2 | 0 | 0 | 3.5 | 3.5
|  | C | 693.28 | 620.08 | 7 | 2 | 4 | 13 | 1 | 2 | 0 | 3 | 7 | 0 | 4 | 11
|  | F | 370.96 | 334.96 | 1 | 1 | 1 | 3 | 0.5 | 1 | 0 | 1.5 | 0.5 | 0 | 1 | 1.5
|  | link | 216.3
| Floor-9 | A | 500.56 | 452.56 | 2 | 1 | 2 | 5 | 1 | 1 | 0 | 2 | 1 | 0 | 2 | 3
|  | B | 248.88 | 227.28 | 1.5 | 1 | 2 | 4.5 | 1 | 1 | 0 | 2 | 0.5 | 0 | 2 | 2.5
|  | C | 693.28 | 620.08 | 1.5 | 1 | 3 | 5.5 | 1 | 1 | 0 | 2 | 0.5 | 0 | 3 | 3.5
|  | link | 216
|  | Total | 13180.28 | 10434.48 | 41 | 27.5 | 67 | 135.5 | 21.5 | 27.5 | 0 | 49 | 19.5 | 0 | 67 | 86.5
|  |  |  | % of Total Day-load | 23.98% | 28.95% | 39.18% | 32.73%
Estimated night-time kWhrs
|  |  |  | for the measured period in July | 9184 | 6160 | 15008 | 30352 | 4816 | 6160 | 0 | 10976 | 4368 | 0 | 15008 | 19376
(80% 14 hours/day, 20 days)
|  | Note: | 1. The night loads on lights, plugs and AC are based on measurements on each service over a 24 hour period.
2. The night load on plugs is in general low and central switching of plugs is not recommended.
3. The potential saving with central switching of lights is relatively low, although central switching of lights is adviseable.
4. The night load on the AC is high and central switching of AC can be considered.

## 6.AC-timeclock
Tender: Energy Audit DME-building: Addendum 6
Department of Mineral and Energy Affairs
contractor: |  | Shared Energy Management (Pty)Ltd |  |  |  |  | compiled: | R.Wyma
|  | PO Box 7270 |  |  |  |  | date: | 2002-08-19
|  | Centurion 0046 |  |  |  |  | ref: | GP0032
Subject: |  | Savings with Time Clock Control on AC:
Calculation of Energy Savings with Time Clock Control on AC
| month | AC-Total | % AC-Total | AC-day | AC-night | Saving | Cost/mnth
| Jan | -57904 | 78% | -45165.12 | -12738.88 | -12738.88 | -1411.4679
| Febr | -57904 | 76% | -44007.04 | -13896.96 | -13896.96 | -1539.7832
| Mch | 97950 | 74% | 72483 | 25467 | 25467 | 2821.7436
| Apr | 71821 | 72% | 51711.12 | 20109.88 | 20109.88 | 2228.1747
| May | 62620 | 70% | 43834 | 18786 | 18786 | 2081.4888
| Jun | 68884 | 68% | 46841.12 | 22042.88 | 22042.88 | 2442.3511 |  | 0.35
| Jul | -57904 | 125.9% | -72912 | 15008 | 15008 | 1662.8864 |  | -2.6269
| Aug | 50230 | 68% | 34156.4 | 16073.6 | 16073.6 | 1780.9549 |  | 3.125
| Sept | -57904 | 70% | -40532.8 | -17371.2 | -17371.2 | -1924.729
| Oct | -57904 | 72% | -41690.88 | -16213.12 | -16213.12 | -1796.4137
| Nov | -57904 | 74% | -42848.96 | -15055.04 | -15055.04 | -1668.0984
| Dec | -57904 | 76% | -44007.04 | -13896.96 | -13896.96 | -1539.7832
| Total | -53823 | 152.6% | -82138.2 | 28315.2 | 28315.2 | 3137.3242
| Average | -4485.25 | 152.6% | -6844.85 | 2359.6 | 2359.6 | 261.4437
| Note: | 1. AC-total kWhrs calculated as per "Year"-data.
2. "% AC-Total" based on assumptions with reference to July.
3. During summer more AC will run and therefore more AC may remain ON after-hours.
| Result: | 1. Annual saving by switching off the AC after-hours for 14 hours = |  |  |  |  | 3137.3242
|  | 2. Cost for 25 DB's to provide time clock control per DB @ R2 500 = |  |  |  |  | 62500
|  | 3. Payback period based on straight payback = |  |  |  |  | 19.9214 | years
Calculations of MD (kVA) Savings with Load Control on AC-Units
| month | DME | %of DME | AC-MD | AC-MD* | saving | R-saving
| Jan | 576 | 52.26% | 301 | 225.75 | 75.25 | 3727.1325
| Febr | 532.8 | 48.39% | 257.8 | 193.35 | 64.45 | 3192.2085
| Mch | 508 | 45.87% | 233 | 174.75 | 58.25 | 2885.1225
| Apr | 440 | 37.5% | 165 | 123.75 | 41.25 | 2043.1125
| May | 442 | 46% | 203.32 | 152.49 | 50.83 | 2517.6099
| Jun | 0 | 46% | 0 | 0 | 0 | 0
| Jul | 403 | 51.36% | 207 | 155.25 | 51.75 | 2563.1775
| Aug | 290.9036 | 46% | 133.8157 | 100.3618 | 33.4539 | 1656.9726
| Sept | 436.8 | 46% | 200.928 | 150.696 | 50.232 | 2487.991
| Oct | 460.8 | 40.32% | 185.8 | 139.35 | 46.45 | 2300.6685
| Nov | 504 | 45.44% | 229 | 171.75 | 57.25 | 2835.5925
| Dec | 523.2 | 47.44% | 248.2 | 186.15 | 62.05 | 3073.3365
| Total | 5117.5036 | 46.21% | 2364.8637 | 1773.6478 | 591.2159 | 29282.9244
| Average | 426.4586 | 46.21% | 197.072 | 147.804 | 49.268 | 2440.2437
| Note: | 1. AC-MD* = revised maximum demand after implementation of demand control at 75%.
2. AC-MD is adjusted for the winter months according to measurements.
3. Saving based on R49.53 / kVA.
4. For DME-kVA data, see the "Account"-data.
| Result: | 1. Annual saving by means of demand control on some AC-units = |  |  |  |  | 29282.9244
|  | 2. Cost for demand control on ± 200 AC-console units @ R500 = |  |  |  |  | 100000
|  | 3. Payback period based on straight payback = |  |  |  |  | 3.415 | years

## 7.1.Light-timeclock
Tender: Energy Audit DME-building: Addendum 7.1
Department of Mineral and Energy Affairs
contractor: |  | Shared Energy Management (Pty)Ltd |  |  |  |  | compiled: | R.Wyma
|  | PO Box 7270 |  |  |  |  | date: | 2002-08-19
|  | Centurion 0046 |  |  |  |  | ref: | GP0032
Subject: |  | Savings with Time Clock Control on Lights:
Assume that 80% of the Night Load on Lights can be Switched OFF:
Time Clock Control on Lights:Reduce Night Load by 80% only
| month | Total | day | night | %-saving | Saving | Cost/mnth
| Jan | 36544 | 27360 | 9184 | 80% | 7347.2 | 814.0698
| Febr | 36544 | 27360 | 9184 | 80% | 7347.2 | 814.0698
| Mch | 36544 | 27360 | 9184 | 80% | 7347.2 | 814.0698
| Apr | 36544 | 27360 | 9184 | 80% | 7347.2 | 814.0698
| May | 36544 | 27360 | 9184 | 80% | 7347.2 | 814.0698
| Jun | 36544 | 27360 | 9184 | 80% | 7347.2 | 814.0698
| Jul | 36544 | 27360 | 9184 | 80% | 7347.2 | 814.0698
| Aug | 36544 | 27360 | 9184 | 80% | 7347.2 | 814.0698
| Sept | 36544 | 27360 | 9184 | 80% | 7347.2 | 814.0698
| Oct | 36544 | 27360 | 9184 | 80% | 7347.2 | 814.0698
| Nov | 36544 | 27360 | 9184 | 80% | 7347.2 | 814.0698
| Dec | 36544 | 27360 | 9184 | 80% | 7347.2 | 814.0698
| Total | 438528 | 328320 | 110208 | 20.11% | 88166.4 | 9768.8371
| Average | 36544 | 27360 | 9184 | 20.11% | 7347.2 | 814.0698
| Note: | 1. Lights-Total kWhrs calculated as per "Year"-data.
2. "% - saving" based on assumptions with some of the lights remaining ON for passages.
3. The number of lights that will remain ON, will vary from day to day.
4. During our night visit, a total of 25% of lights in the offices were ON.
5. The light-load during night based on measurements as per "Night-Savings"
| Result: | 1. Annual saving by switching off the Lights after-hours for 14 hours = |  |  |  |  | 9768.8371
|  | 2. Cost for 25 DB's to provide time clock control per DB @ R1 500 = |  |  |  |  | 37500
|  | 3. Payback period based on straight payback = |  |  |  |  | 3.8387 | years
Assume that over and above the Night Load, 25% of the Day Load remains ON:
Time Clock Control on Lights:Reduce 25% of Lights ON + 80% night load
|  | Saving | 80%of 25% | Total |  |  | Cost/mnth
| month | as above | of day load | Saving | % saving |  | Cost/mnth
| Jan | 7347.2 | 5472 | 12819.2 | 35.08% |  | 1420.3674
| Febr | 7347.2 | 5472 | 12819.2 | 35.08% |  | 1420.3674
| Mch | 7347.2 | 5472 | 12819.2 | 35.08% |  | 1420.3674
| Apr | 7347.2 | 5472 | 12819.2 | 35.08% |  | 1420.3674
| May | 7347.2 | 5472 | 12819.2 | 35.08% |  | 1420.3674
| Jun | 7347.2 | 5472 | 12819.2 | 35.08% |  | 1420.3674
| Jul | 7347.2 | 5472 | 12819.2 | 35.08% |  | 1420.3674
| Aug | 7347.2 | 5472 | 12819.2 | 35.08% |  | 1420.3674
| Sept | 7347.2 | 5472 | 12819.2 | 35.08% |  | 1420.3674
| Oct | 7347.2 | 5472 | 12819.2 | 35.08% |  | 1420.3674
| Nov | 7347.2 | 5472 | 12819.2 | 35.08% |  | 1420.3674
| Dec | 7347.2 | 5472 | 12819.2 | 35.08% |  | 1420.3674
| Total | 88166.4 | 65664 | 153830.4 |  |  | 17044.4083
| Average | 7347.2 | 5472 | 12819.2 |  |  | 1420.3674
| Note: | 1. Lights-Total kWhrs calculated as per "Year"-data.
2. "% - saving" based on assumptions with all lights off.
3. The number of lights that will remain ON, will vary from day to day.
4. During our night visit, a total of 25% of lights in the offices were ON.
5. The light-load during night based on measurements as per "Night-Savings"
|  | 6. Saving of 25% on lights (dayload of 27 360 kWhr) = |  |  |  | 6840 | kWhrs
| Result: | 1. Annual saving by switching off the Lights after-hours for 14 hours = |  |  |  |  | 17044.4083
|  | 2. Cost for 25 DB's to provide time clock control per DB @ R1 500 = |  |  |  |  | 37500
|  | 3. Payback period based on straight payback = |  |  |  |  | 2.2001 | years

## 7.2.Light Time+Switch
Tender: Energy Audit DME-building: Addendum 7.2
Department of Mineral and Energy Affairs
contractor: |  | Shared Energy Management (Pty)Ltd |  |  |  |  | compiled: | R.Wyma
|  | PO Box 7270 |  |  |  |  | date: | 2002-08-19
|  | Centurion 0046 |  |  |  |  | ref: | GP0032
Subject: |  | Savings with Time Clock Control on Lights
and Additional Day-Night Switches for the North Side:
From Addendum 7.1: Provide separate control for North and South Zones:
Time Clock Control on Lights and Day-Night Switches for North Side
|  | Saving | % off of | Power on | Saving on | Total | Cost/mnth
| month | as per 7.1 | North Side | North Side | North Side | Saving | Cost/mnth
| Jan | 12819.2 | 0% | 10944 | 0 | 12819.2 | 1420.3674
| Febr | 12819.2 | 10% | 10944 | 1094.4 | 13913.6 | 1541.6269
| Mch | 12819.2 | 20% | 10944 | 2188.8 | 15008 | 1662.8864
| Apr | 12819.2 | 40% | 10944 | 4377.6 | 17196.8 | 1905.4054
| May | 12819.2 | 60% | 10944 | 6566.4 | 19385.6 | 2147.9245
| Jun | 12819.2 | 80% | 10944 | 8755.2 | 21574.4 | 2390.4435
| Jul | 12819.2 | 80% | 10944 | 8755.2 | 21574.4 | 2390.4435
| Aug | 12819.2 | 60% | 10944 | 6566.4 | 19385.6 | 2147.9245
| Sept | 12819.2 | 40% | 10944 | 4377.6 | 17196.8 | 1905.4054
| Oct | 12819.2 | 20% | 10944 | 2188.8 | 15008 | 1662.8864
| Nov | 12819.2 | 10% | 10944 | 1094.4 | 13913.6 | 1541.6269
| Dec | 12819.2 | 0% | 10944 | 0 | 12819.2 | 1420.3674
| Total | 153830.4 |  | 131328 | 45964.8 | 199795.2 | 22137.3082
| Average | 12819.2 |  | 10944 | 3830.4 | 16649.6 | 1844.7757
| Note: | 1. Saving by means of time clock control as per Addendum 7.1 = |  |  |  |  | 12819.2 | kWhrs
2. "% - off" based on assumptions with natural light through north side windows.
3. Each DB to be provided with 2 zones of time clock control, now 50 zones.
4. Cost for 50 zones of time clock control for 25 DB's now double.
5. Day-night switches to be provided for 25 north zones @ R500 each.
|  | 6. Total power consumption of lights per month during the day = |  |  |  |  | 27360 | kWhrs
|  | 7. Power consumption of Lights on the North Side at |  |  |  | 40% | 10944 | kWhrs
| Result: | 1. Annual saving with time clock control and day-night switches = |  |  |  |  | 22137.3082
|  | 2. Cost for 50 zones @ R1 500 and 25 day-night switches @ R500 = |  |  |  |  | 87500
|  | 3. Payback period based on straight payback = |  |  |  |  | 3.9526 | years

## 7.3 Lights+Bonesa
Tender: Energy Audit DME-building: Addendum 7.3
Department of Mineral and Energy Affairs
contractor: |  | Shared Energy Management (Pty)Ltd |  |  |  |  | compiled: | R.Wyma
|  | PO Box 7270 |  |  |  |  | date: | 2002-08-19
|  | Centurion 0046 |  |  |  |  | ref: | GP0032
Subject: |  | Time Clock Control on Lights with
BONESA Report implemented
As per Addendum 7.1 and with reference to BONESA Report, page 9:
Assume that 80% of the Night Load on Lights can be Switched OFF:
Time Clock Control on Lights:Reduce Night Load by 80% only
| month | Total | day | night | %-saving | Saving | Cost/mnth
| Jan | 16564.4167 | 12401.5554 | 4162.8613 | 80% | 3330.289 | 368.996
| Febr | 16564.4167 | 12401.5554 | 4162.8613 | 80% | 3330.289 | 368.996
| Mch | 16564.4167 | 12401.5554 | 4162.8613 | 80% | 3330.289 | 368.996
| Apr | 16564.4167 | 12401.5554 | 4162.8613 | 80% | 3330.289 | 368.996
| May | 16564.4167 | 12401.5554 | 4162.8613 | 80% | 3330.289 | 368.996
| Jun | 16564.4167 | 12401.5554 | 4162.8613 | 80% | 3330.289 | 368.996
| Jul | 16564.4167 | 12401.5554 | 4162.8613 | 80% | 3330.289 | 368.996
| Aug | 16564.4167 | 12401.5554 | 4162.8613 | 80% | 3330.289 | 368.996
| Sept | 16564.4167 | 12401.5554 | 4162.8613 | 80% | 3330.289 | 368.996
| Oct | 16564.4167 | 12401.5554 | 4162.8613 | 80% | 3330.289 | 368.996
| Nov | 16564.4167 | 12401.5554 | 4162.8613 | 80% | 3330.289 | 368.996
| Dec | 16564.4167 | 12401.5554 | 4162.8613 | 80% | 3330.289 | 368.996
| Total | 198773 | 148818.6646 | 49954.3354 | 20.11% | 39963.4683 | 4427.9523
| Average | 16564.4167 | 12401.5554 | 4162.8613 | 20.11% | 3330.289 | 368.996
| Note: | 1. Lights-Total kWhrs as per Bonesa Report = |  |  |  | 198773 | kWhrs
|  | 2. % remaining power from original |  |  | 438528 | 45.33%
3. "% - saving" based on assumptions with some of the lights remaining ON for passages.
4. The number of lights that will remain ON, will vary from day to day.
5. During our night visit, a total of 25% of lights in the offices were ON.
6. The light-load during night based on measurements as per "Night-Savings"
| Result: | 1. Annual saving by switching off the Lights after-hours for 14 hours = |  |  |  |  | 4427.9523
|  | 2. Cost for 25 DB's to provide time clock control per DB @ R1 500 = |  |  |  |  | 37500
|  | 3. Payback period based on straight payback = |  |  |  |  | 8.4689 | years
Assume that over and above the Night Load, 25% of the Day Load remains ON:
Time Clock Control on Lights:Reduce 25% of Lights ON + 80% night load
|  | Saving | 80%of 25% | Total |  |  | Cost/mnth
| month | as above | of day load | Saving | % saving |  | Cost/mnth
| Jan | 3330.289 | 2480.3111 | 5810.6001 | 35.08% |  | 643.8145
| Febr | 3330.289 | 2480.3111 | 5810.6001 | 35.08% |  | 643.8145
| Mch | 3330.289 | 2480.3111 | 5810.6001 | 35.08% |  | 643.8145
| Apr | 3330.289 | 2480.3111 | 5810.6001 | 35.08% |  | 643.8145
| May | 3330.289 | 2480.3111 | 5810.6001 | 35.08% |  | 643.8145
| Jun | 3330.289 | 2480.3111 | 5810.6001 | 35.08% |  | 643.8145
| Jul | 3330.289 | 2480.3111 | 5810.6001 | 35.08% |  | 643.8145
| Aug | 3330.289 | 2480.3111 | 5810.6001 | 35.08% |  | 643.8145
| Sept | 3330.289 | 2480.3111 | 5810.6001 | 35.08% |  | 643.8145
| Oct | 3330.289 | 2480.3111 | 5810.6001 | 35.08% |  | 643.8145
| Nov | 3330.289 | 2480.3111 | 5810.6001 | 35.08% |  | 643.8145
| Dec | 3330.289 | 2480.3111 | 5810.6001 | 35.08% |  | 643.8145
| Total | 39963.4683 | 29763.7329 | 69727.2012 |  |  | 7725.7739
| Average | 3330.289 | 2480.3111 | 5810.6001 |  |  | 643.8145
| Note: | 1. Lights-Total kWhrs calculated as per BONESA Report
2. "% - saving" based on assumptions with all lights off.
3. The number of lights that will remain ON, will vary from day to day.
4. During our night visit, a total of 25% of lights in the offices were ON.
5. The light-load during night based on measurements as per "Night-Savings"
|  | 6. Saving of 25% on lights (dayload of 12 402 kWhr) = |  |  |  | 3100.3888 | kWhrs
| Result: | 1. Annual saving by switching off the Lights after-hours for 14 hours = |  |  |  |  | 7725.7739
|  | 2. Cost for 25 DB's to provide time clock control per DB @ R1 500 = |  |  |  |  | 37500
|  | 3. Payback period based on straight payback = |  |  |  |  | 4.8539 | years

## 8.AC Heat load
Tender: Energy Audit DME-building: Addendum 8
Department of Mineral and Energy Affairs
contractor: |  | Shared Energy Management (Pty)Ltd |  |  |  |  | compiled: | R.Wyma
|  | PO Box 7270 |  |  |  |  | date: | 2002-08-19
|  | Centurion 0046 |  |  |  |  | ref: | GP0032
Subject: |  | Options with Cooling Load Reductions
Cooling Loads for a Typical Office with diffirent Options (Watt): NORTH
| month | 1.Existing | 2.Insul Panel | 3.Reduce Glass | 4.Film on Glass | Saving(W/y) | Save/mnth
| Jan | 1793 | 1736 | 1656 | 1579 | 34240 | 1.8969
| Febr | 1823 | 1712 | 1655 | 1553 | 43200 | 2.3933
| Mch | 1803 | 1716 | 1641 | 1549 | 40640 | 2.2515
| Apr | 1924 | 1852 | 1667 | 1602 | 51520 | 2.8542
| May | 1898 | 1811 | 1681 | 1532 | 58560 | 3.2442
| Jun | 1896 | 1792 | 1592 | 1496 | 64000 | 3.5456
| Jul | 1791 | 1723 | 1505 | 1424 | 58720 | 3.2531
| Aug | 1687 | 1593 | 1463 | 1432 | 40800 | 2.2603
| Sept | 1651 | 1560 | 1492 | 1411 | 38400 | 2.1274
| Oct | 1586 | 1550 | 1486 | 1391 | 31200 | 1.7285
| Nov | 1632 | 1577 | 1483 | 1403 | 36640 | 2.0299
| Dec | 1757 | 1687 | 1575 | 1503 | 40640 | 2.2515
| Total | 21241 | 20309 | 18896 | 17875 | 538560 | 29.8362
| Average | 1770.0833 | 1692.4167 | 1574.6667 | 1489.5833 | 44880 | 2.4864
| Note: | 1. Typical office is half a module = 16.2 m²
2. Cooling Saving/year = (1.Existing - 4.Film on Glass) x 20 days/month x 10 hrs/day x 0.8 diversity
3. Saving = R0.1108/kWhr x cooling saving/year ÷ COP of 2
4. Glass area per office = 5 m².
5. Number of North Offices = (7 x 19 modules in Phase 1) + (18 modules in Phase 2) x 2 offices/module
= 151 modules x 2 = 302 offices
| Result: | 1. Annual saving by providing film on the north windows = |  |  |  |  | 29.8362
|  | 2. Cost to provide film on glass of 5 m² @ R150/m² = |  |  |  |  | 750
|  | 3. Payback period based on straight payback = |  |  |  |  | 25.1372 | years
|  | 4. Total estimated cost for film on 302 north offices @ 5m²/office and R150/m² = |  |  |  |  | 226500
Cooling Loads for a Typical Office with diffirent Options (Watt): SOUTH
| month | 1.Existing | 2.Insul Panel | 3.Reduce Glass | 4.Film on Glass | Saving(W/y) | Save/mnth
| Jan | 1815 | 1748 | 1605 | Not Applicable | 10720 | 0.59389
| Febr | 1682 | 1602 | 1516 |  | 12800 | 0.70912
| Mch | 1522 | 1473 | 1385 |  | 7840 | 0.43434
| Apr | 1355 | 1321 | 1269 |  | 5440 | 0.30138
| May | 1185 | 1158 | 1091 |  | 4320 | 0.23933
| Jun | 1073 | 1062 | 1016 |  | 1760 | 0.097504
| Jul | 1043 | 1023 | 982 |  | 3200 | 0.17728
| Aug | 1176 | 1154 | 1097 |  | 3520 | 0.19501
| Sept | 1358 | 1321 | 1261 |  | 5920 | 0.32797
| Oct | 1488 | 1395 | 1322 |  | 14880 | 0.82435
| Nov | 1649 | 1598 | 1508 |  | 8160 | 0.45206
| Dec | 1821 | 1768 | 1636 |  | 8480 | 0.46979
| Total | 17167 | 16623 | 15688 | 0 | 87040 | 4.822
| Average | 1430.5833 | 1385.25 | 1307.3333 | 0 | 7253.3333 | 0.40183
| Note: | 1. Typical office is half a module = 16.2 m²
2. Cooling Saving/year = (1.Existing - 2. Insulate Panel) x 20 days/month x 10 hrs/day x 0.8 diversity
3. Saving = R0.1108/kWhr x cooling saving/year ÷ COP of 2
4. Panel area per office = 2 m².
5. Number of South Offices = (7 x 19 modules in Phase 1) + (18 modules in Phase 2) x 2 offices/module
= 151 modules x 2 = 302 offices
| Result: | 1. Annual saving by providing insulation on wall panels = |  |  |  |  | 4.822
|  | 2. Cost to provide insulation panel on wall of 2 m² @ R250/m² = |  |  |  |  | 500
|  | 3. Payback period based on straight payback = |  |  |  |  | 103.6911 | years
|  | 4. Total estimated cost for film on 302 south offices @ 2m²/office and R250/m² = |  |  |  |  | 151000

## 13. lights
Tender: Energy Audit DME-building: Addendum 13
Department of Mineral and Energy Affairs
contractor: | Shared Energy Management (Pty)Ltd |  |  |  |  | compiled: | R.Wyma
| PO Box 7270 |  |  |  |  | date: | 2002-08-19
| Centurion 0046 |  |  |  |  | ref: | GP0032
Subject: | Lighting Lux Levels in Offices
Typical Lighting Lux Levels in the Offices:
| Notes: | 1. Measured directly underneath the light fitting at desk height of 800 mm.
2. The floor to ceiling height = 2 350 mm.
3. The fittings are resessed into the coffer slab of 350 mm deep.
4. Therefore the total height from floor to underside of fitting = 2 700 mm.
5. Colour of concrete ceiling (slab) = sand stone
6. Minimum adviseable lighting level for offices = 300 lux.
| South Side | No. of Tubes | condition | open curtain | closed curtain
15h00
|  | 2 | old tubes | 300 | 250
|  | 1 | old tubes | 250 | 200
|  |  | Difference = | 50 | 50
| North Side | No. of Tubes | condition | open curtain | closed curtain
15h00
|  | 2 | old tubes | 500 | 350
|  | 1 | old tubes | 450 | 300
|  |  | Difference = | 50 | 50
Night Time:
| No. of tubes | condition | 2m to the | directly | 2 m to the right
|  | of tubes | left | underneath | against wall
| normal height | old | 200 | 240 | 160
| lowered | old | 250 | 310 | 200
|  | Difference = | 50 | 70 | 40
Night Time:
| No. of tubes | condition | 2m to the | directly | 2 m to the right
|  | of tubes | left | underneath | against wall
| normal height | new | 330 | 380 | 280
| lowered | new | 360 | 500 | 350
|  | Difference = | 30 | 120 | 70
Power Consumption:
| condition | Measured | 2 x 1 500 tube | Total Power | Power of
| of tubes | current (Amp) | Watt each | Consumption | Ballast (Watt)
| old | 0.8 | 58 | 184 | 68
| new | 0.8 | 58 | 184 | 68
|  | Difference = | 0 | 0 | 0
| Conclusions: | 1. Replacing the old tubes with new tubes has a tremendous effect.
2. Lowering the light fitting out of the coffer slab is adviseable.
3. The distribution of light to the sides are improved with the lowered position.
4. The power consumption of the ballast is high, 37%. Normally 25%.
5. A large number of light fittings is not in a working condition.
6. A tube that is only slighty glowing, consumes the same amount of power.

## 14.Incandes
DME Energy Audit: Addendum 14
contractor: |  | Shared Energy Management (Pty)Ltd | [11 empty] | compiled: | R.Wyma
|  | PO Box 7270 | [11 empty] | date: | 2002-08-08
|  | Centurion 0046 | [11 empty] | ref: | GP0032
Subject: |  | Replacement of Incandescent Lights
|  |  | Areas (m²) |  |  | Incandescent |  |  | Fluorescent |  |  | Savings per Year
| Floor | Block | Gross | Net | No. | Watt | Power | No. | Watt | Power | Power | Hours | Cost | Saving
| Floor-3 | A | 500.56 | 452.56 | 8 | 100 | 0.8 | 8 | 15 | 0.12 | 0.68 | 8760 | 0.11 | 655.248
|  | B | 248.88 | 227.28 | 4 | 100 | 0.4 | 4 | 15 | 0.06 | 0.34 | 8760 | 0.11 | 327.624
|  | C | 693.28 | 620.08 | 11 | 100 | 1.1 | 11 | 15 | 0.165 | 0.935 | 8760 | 0.11 | 900.966
|  | link | 216.3
| Floor-4 | A | 500.56 | 452.56 | 8 | 100 | 0.8 | 8 | 15 | 0.12 | 0.68 | 8760 | 0.11 | 655.248
|  | B | 248.88 | 227.28 | 4 | 100 | 0.4 | 4 | 15 | 0.06 | 0.34 | 8760 | 0.11 | 327.624
|  | C | 693.28 | 620.08 | 11 | 100 | 1.1 | 11 | 15 | 0.165 | 0.935 | 8760 | 0.11 | 900.966
|  | link | 216.3
| Floor-5 | A | 500.56 | 452.56 | 8 | 100 | 0.8 | 8 | 15 | 0.12 | 0.68 | 8760 | 0.11 | 655.248
|  | B | 248.88 | 227.28 | 4 | 100 | 0.4 | 4 | 15 | 0.06 | 0.34 | 8760 | 0.11 | 327.624
|  | C | 693.28 | 620.08 | 11 | 100 | 1.1 | 11 | 15 | 0.165 | 0.935 | 8760 | 0.11 | 900.966
|  | link | 216.3
| Floor-6 | A | 500.56 | 452.56 | 8 | 100 | 0.8 | 8 | 15 | 0.12 | 0.68 | 8760 | 0.11 | 655.248
|  | B | 248.88 | 227.28 | 4 | 100 | 0.4 | 4 | 15 | 0.06 | 0.34 | 8760 | 0.11 | 327.624
|  | C | 693.28 | 620.08 | 11 | 100 | 1.1 | 11 | 15 | 0.165 | 0.935 | 8760 | 0.11 | 900.966
|  | D | 376.96 | 340.96 | 8 | 100 | 0.8 | 8 | 15 | 0.12 | 0.68 | 8760 | 0.11 | 655.248
|  | E | 360.16 | 324.16 | 8 | 100 | 0.8 | 8 | 15 | 0.12 | 0.68 | 8760 | 0.11 | 655.248
|  | F | 370.96 | 334.96 | 8 | 100 | 0.8 | 8 | 15 | 0.12 | 0.68 | 8760 | 0.11 | 655.248
|  | link | 304.7
| Floor-7 | A | 500.56 | 452.56 | 8 | 100 | 0.8 | 8 | 15 | 0.12 | 0.68 | 8760 | 0.11 | 655.248
|  | B | 248.88 | 227.28 | 4 | 100 | 0.4 | 4 | 15 | 0.06 | 0.34 | 8760 | 0.11 | 327.624
|  | C | 693.28 | 620.08 | 11 | 100 | 1.1 | 11 | 15 | 0.165 | 0.935 | 8760 | 0.11 | 900.966
|  | link | 216.3
| Floor-8 | A | 500.56 | 452.56 | 8 | 100 | 0.8 | 8 | 15 | 0.12 | 0.68 | 8760 | 0.11 | 655.248
|  | B | 248.88 | 227.28 | 4 | 100 | 0.4 | 4 | 15 | 0.06 | 0.34 | 8760 | 0.11 | 327.624
|  | C | 693.28 | 620.08 | 11 | 100 | 1.1 | 11 | 15 | 0.165 | 0.935 | 8760 | 0.11 | 900.966
|  | F | 370.96 | 334.96 | 8 | 100 | 0.8 | 8 | 15 | 0.12 | 0.68 | 8760 | 0.11 | 655.248
|  | link | 216.3
| Floor-9 | A | 500.56 | 452.56 | 8 | 100 | 0.8 | 8 | 15 | 0.12 | 0.68 | 8760 | 0.11 | 655.248
|  | B | 248.88 | 227.28 | 4 | 100 | 0.4 | 4 | 15 | 0.06 | 0.34 | 8760 | 0.11 | 327.624
|  | C | 693.28 | 620.08 | 11 | 100 | 1.1 | 11 | 15 | 0.165 | 0.935 | 8760 | 0.11 | 900.966
|  | link | 216
|  | Total | 13180.28 | 10434.48 | 193 |  | 19.3 | 193 |  | 2.895 | 16.405 |  |  | 15807.858
[13 empty] | Intalled Cost per New Light Fitting = | 200
[13 empty] | Number of Light Fittings = | 193
[13 empty] | Total Capital Cost for Light Fittings = | 38600
[13 empty] | Estimated Savings per Year = | 15807.858
[13 empty] | Payback in Years = | 2.4418
| Notes: | 1. Lights in passages and staircases shall be on full time.
2. The replacement of the old bulb with a new CFL-light is not recommended because the fittings are old.
0